## Medical Service Related Informa
SL No | Office | District Name | Name of the Hospital | Upazilla | Filled up Form | Remarks
1 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Fakirhat Upazila Health Complex | fakirhat | 1 xlsx
2 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Mollahat Upazila Health Complex | mollahat | 1 xlsx
3 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazilla Health Complex | chitalmari | 1 xlsx
4 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | 1 xlsx
5 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | 1 xlsx
6 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | No file
7 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal | No file
8 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | 1 xlsx

## General Information
SL No | Office | District Name | Name of the Hospital | Upazilla | Year of Establishment | Construction agency | Availability of Additional Land | Number of Beds of Existing Hospital Building | Digital Survey Map (CAD and PDF) | Soil Test Report (click i button for detail) | As Built Arc Drawing of Existing Hospital Building (Floor Plans) | Layout of Hospital (At least Hand Drawn) | Plinth Area of Existing Hospital Bldg (sqft) | Floor Area (sft by each floor) | Master Plan of Campus (Demarking Visually Vulnerable Buildings) | Attach Land Records (if any) | Visual Evidence of the area (Image or video) | Flood Level Information | Remarks (Additional Information)
1 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Fakirhat Upazila Health Complex | fakirhat | 2012 | HED | Available | 50 | 1 dwg | No file | 1 pdf | 1 pdf | 8601 | 8601, 8256,6390 | 1 dwg | No file | 3 jpegs | H.F=G.L+1 | Land Area:7.23 acre
2 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Mollahat Upazila Health Complex | mollahat | 2012 | HED | Available | 50 | 1 dwg | No file | 1 pdf | 1 pdf | 8601 | 8601, 8256,6390 | 1 dwg | No file | 3 jpegs | H.F=G.L+2 | Land Area: 4.05 acre
3 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazilla Health Complex | chitalmari | 2012 | HED | 21630 sft area ( if pond is filled up) | 31 | 1 dwg | No file | 1 pdf | 1 pdf | 8601 | 8601.8256, 4110 | 1 dwg | No file | 4 jpegs | H.F+1'
4 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | 2005 | HED | Available | 19 | 1 dwg | No file | 1 pdf | 1 pdf | 8601 | 8601, 8256 | 1 dwg | No file | 1 jpeg | 3' above
5 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | 2010 | HED | Available | 50 | 1 dwg | No file | No file | 1 pdf |  | 6000 | No file | 1 jpeg | 1 jpeg | 3'-6" above | 31 শয্যা হাসপাতাল টি ০১/০৭/২০২৫ তারিখে পরিত্যক্ত ঘোষনা করা হয়েছে। ৯ শয্যা বিশিষ্ট ৩য় তলা ভবনে চিকিৎসা কার্যক্রম চলামান আছে।
6 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | 1962 | Other | Available | 19 | 1 dwg | No file | No file | 1 pdf |  | 7750 | No file | No file | 1 jpeg | 3'-6" | বর্তমানে ১৯ শয্যা বিশিষ্ট ৩য় তলা ভবনে চিকিৎসা কার্যক্রম চলামান আছে। ২০১২ সালে ৫০ শয্যা বিশিষ্ট হাসপাতাল উন্নীতকরন করা হয় এবং ৩১ শয্যা বিশিষ্ট হাসপাতাল ভবন HED কতৃক নির্মানাধীন রয়েছে।
7 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal | 2022 | HED | Available | 50 | 1 dwg | No file | No file | 1 pdf |  | 6500 | No file | 1 jpeg | 1 jpeg | 3'-6" | ৬ তলা ফাউন্ডেশন বিশিষ্ট ৩য় তলায় ৩১ বেডের কার্যক্রম চলমান রয়েছে। পাশেই ২০০৯ সালে নির্মিত ১৯ শয্যার হাসপাতাল চলমান আছে।
8 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | 1985 | HED | Available | 50 | 1 dwg | No file | No file | 1 pdf |  | 9200 | No file | No file | 1 jpeg | 4'-0" | বর্তমানে ১৯ শয্যা বিশিষ্ট ৩য় তলা ভবনে চিকিৎসা কার্যক্রম চলামান আছে। ৩১ শয্যা বিশিষ্ট ২য় তলা ভবনটি ২৮/১০/২০২৫ তারিখে HED পরিত্যাক্ত ঘোষণা করে। কিন্তু স্বাস্থ্য সেবা চালিয়া রাখার জন্য পরিত্যাক্ত ভবনটি ঝুকি নিয়ে ব্যবহার করা হচ্ছে।

## Civil Related
SL No | Office | District Name | Name of the Hospital | Upazilla | Building Height (PL to Top in ft) | PL Height (EGL to PL in ft) | Existing Floor Number | Foundation Type | Foundation Capacity (floor number) | Structure Type | Structural Condition of Main Hospital Bldg (Describe) | Structural Assessment Report | Vertical Extension (possible or not-possible) | Previous Renovation History | Remarks (Additional Information)
1 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Fakirhat Upazila Health Complex | fakirhat | 30 | 2.5 | 3 | Deep | 4 | RCC | Coloum Size =21"836" ,21"*18",21*13" Span =18' | No file | Not Possible |  | 1.Construction of new boundary wall 2. in crease of Internal Road hight 3.Provision of safe drinking Water facilities (3)old building :Bed 19,Office ,imergency,Lab section , X ray, Store,4 ward (4) New Building :OPD,Farmecy,I centre, Dengu Ward ,Room, cabin
2 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Mollahat Upazila Health Complex | mollahat | 30 | 2.5 | 3 | Deep | 4 | RCC | Coloum Size =21"836" ,21"*18",21*13" Span =18' | No file | Not Possible |  | *১টি পরিত্যক্ত ভবন কোন কার্যক্রম নাই * নতুন বিল্ডিং এ জলছাদ আছে * ১টি গভীর নলকূল আছে, + submersible *অন্য কোন পানির উৎস নাই *পৌরসভা, ওয়াটার পানির লাইন নাই * পানি নিষ্কাশনের ব্যবস্থা নাই,
3 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazilla Health Complex | chitalmari | 30 | 1.5 | 3 | Footing | 3 | RCC | Structural condition of main hospital building is at a moderate level. Structural defects have become visible in some areas of the building's column, beam & slab. | No file | Not Possible | Regular civil ( plaster, paint sanitary work) & electrical maintenance works have been undertaken.
4 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | 22 | 1.66 | 2 | Footing | 3 | RCC |  | No file | Not Possible |  | In 1980, the facility had a total of 31 beds. Over time, due to natural causes, this number gradually decreased. Several beds became unusable because of deterioration, and some were rendered non‑functional. As a result, the facility could no longer maintain the original capacity of 31 beds. In 2005, an additional 19 beds were added. These newly added beds were also incorporated into the national database. Among the 50 beds listed in the national database, 19 were newly added, while the remaining 31 had gradually become unusable over the years due to natural causes. Among the 19 newly added beds, 3 were designated for female patients. These 3 beds were included in the national database in alignment with the government’s initiative to ensure dedicated facilities for women. Necessary government support and facilities were also allocated for these beds.
5 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | 42 | 2.5 | 3 | Footing | 3 | RCC | Good/New | No file | Not Possible | NA | ১৯ শয্যা বিশিষ্ট ৩য় তলা ভবন এর তথ্য। পরিত্যক্ত ভবনটি উপেক্ষা করা হয়েছে।
6 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | 42 | 2.5 | 3 | Footing | 3 | RCC | Good | No file | Not Possible | NA
7 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal | 42 | 2.5 | 3 | Footing | 6 | RCC | Good | No file | Possible | NA | 31 শয্যা হাসপাতাল এর তথ্য
8 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | 42 | 3 | 3 | Footing | 3 | RCC | Good/New | No file | Not Possible | NA | ১৯ শয্যা বিশিষ্ট ৩য় তলা ভবন এর তথ্য। পরিত্যক্ত ভবনটি উপেক্ষা করা হয়েছে।

## Water Supply and Sanitation
SL No | Office | District Name | Name of the Hospital | Upazilla | Capacity of Existing UGWR (gal) | Number of Deep Tubewell | Additional Water Supply Facility (Describe) | Sewage or Waste Management Facility | Capacity of Sewerage or waste management (cft) | Presence of Rainwater Harvesting Facility | Capacity of Rain Water Harvesting (gal) | Existing Drainage Facility (Describe) | Required Drainage Facility (Describe) | Nearest Waste & Water Disposal Location (Describe) | Remarks (Any other issues will be Described here)
1 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Fakirhat Upazila Health Complex | fakirhat | 0 | 1 |  | Septic Tank |  | No | 0 | around only main building | Required forTotal project area |  | 1. Water supply system improvement 2.Waste management facilities
2 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Mollahat Upazila Health Complex | mollahat | 0 | 1 |  | Septic Tank | 0 | No | 0 | around only main building | Required forTotal project area
3 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazilla Health Complex | chitalmari | 30000 | 1 | pond | Septic Tank |  | No |  | Apron is provided around the building and surface drain is available along the boundary. This appear to be adequate for proper drainage of rainwater and surface runoff. |  | At a abandoned area situated approximately 40 feet from the building.
4 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | 0 | 0 | Water is taken from the campus pond, purified through a filter system, and then used in the hospital | Septic Tank | 10000 | No | 0 | The surface drain is dilapidated and does not provide proper drainage. Due to the inability to drain rainwater, waterlogging occurs | The construction of both the surface drain and the master drain is urgently required.
5 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla |  | 0 | Rain water | Septic Tank |  | Yes | 20000 | poor | RCC Drain |  | কোস্টাল এরিয়া হওয়ায় ডীপ-টিউবওয়েল এর লেয়ার পাওয়া যায় না।
6 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj |  | 0 | Rain water | Septic Tank |  | Yes | 20000 | poor |  | NA
7 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal |  | 0 | Rain water | Septic Tank |  | No | 0 | poor | RCC Drain
8 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | 0 | 0 | Rain water | Septic Tank |  | No | 20000 | poor | RCC Drain | NA

## Ancillary Civil Items
SL No | Office | District Name | Name of the Hospital | Upazilla | Existing boundary wall with retaining wall (ft) | Existing boundary wall without retaining wall (ft) | Additionally Required boundary wall with retaining wall (ft) | Additionally Required boundary wall without retaining wall (ft) | Width of The Main Road (Municipality or City Corp) In front of Hospital (ft) | Internal Road Scenario (Describe) | Existence of Link Corridor | Requirement of Site Improvement | Remarks (additional information)
1 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Fakirhat Upazila Health Complex | fakirhat |  | 1719 |  | 100 | 20 | 10' road | Yes | Yes
2 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Mollahat Upazila Health Complex | mollahat |  | 1719 |  | 100 | 20 | 10' road | Yes | Yes
3 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazilla Health Complex | chitalmari |  | 1703 |  |  | 12 | Internal road is constructed of RCC with a width of 15.5 feet. The current condition of the road is quite good. | Yes | Yes
4 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | 0 | 2099 |  |  | 10 | RCC | Yes | Yes
5 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla |  | 1800 | 0 | 2000 | 15 | good | Yes | Yes
6 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | 0 | 2200 | 300 | 1900 | 18 | poor | Yes | Yes
7 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal |  | 2050 |  | 2200 | 20 | very good | Yes | Yes
8 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | 1850 | 0 | 315 | 1535 | 12 | poor | Yes | Yes

## Electromechanical Items
SL No | Office | District Name | Name of the Hospital | Upazilla | Present Number of Lift | Number of Usable Lift (if present) | Lift Related Additional Info (If any) | Present AC Capacity (Ton) | Additional AC Requirement (Ton) | AC Related Additional Info (If any) | Present Situation of Fire Detection and Protection System | Present Total HP of Submersible Pump | Present Total HP of Centrifugal Pump | Pump Related Additional Info (Demand, Repair need etc) | Medical Waste Management System | Medical Waste Related Additional info (Capacity, Demand etc)
1 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazila Health complex | chitalmari | 0 | 0 | 0 | 10 | 20 |  | no | 0 | 1 | 1 nos 10 hp and 2 nos 2 hp Centifugal pum motor reqired | Not Present | no
2 | Division - Bagerhat PWD Division | Bagerhat | Kachua Upazila Health complex | kachua | 0 | 0 |  | 8 | 20 |  | no | 0 | 4 | 2 nos 10 hp and 2 nos 1 hp Centifugal pum motor reqired | Not Present
3 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | 0 | 0 |  | 30 | 100 | Repair & Maintenance Needed | 15 Nos Fire Extinguisher is Available & 40 Nos is Required | 0 | 2 | 2 HP Centrifugal Or JET Pump - 2 Nos is Required | Incinerator Type | 1 No Incineration Type Needed
4 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | 0 | 0 |  | 9.5 | 20 |  | no |  | 7.5 | 1 nos 10 hp and 2 nos 2 hp Centifugal pum motor reqired | Not Present
5 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal | 0 | 0 | Lift Core Available | 30 | 30 | Repair & Maintenance Needed | 0 | 2 | 0 | Needed , 2 HP Submersible - 2 Nos, 2 HP Centrifugal Or JET Pump - 2 Nos. | Not Present | 1 No Incineration Type Needed
6 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | 0 | 0

## External Electrification
SL No | Office | District Name | Name of the Hospital | Upazilla | Connection Provider | Can Provider Provide Apprx 1250 kVA Load? | Existing Actual Usage of Power or Load (kVA) | Present Total KVA Capacity of Substation | Reusable KVA of substation | Situation of Substation Components (LT HT PFI MDB etc) | Existing Total KVA Capacity of Generator | Additional Requirement of Generator (KVA) | Present Usable Capacity of on grid solar (kWp) | Present Capacity of Ring Main Unit (number of out going connection) | Detailed Description of incoming Service Cable (RM, Type and Length of HT or LT) | Detailed Description of Service Cable (RM and Length for FDB, MDB, ELT, NLT etc) | Remarks (Provide any additional information here)
1 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazila Health complex | chitalmari | REB | Yes |  | 0 |  | no | 10 | 50 |  |  | 15rm wap ,20 meter, | Dilapidated | Dilapidated and almos wasted
2 | Division - Bagerhat PWD Division | Bagerhat | Kachua Upazila Health complex | kachua | REB | Yes | 0 |  |  | no | 10 | 50 |  |  | 25rm wap ,15 meter, | Dilapidated | Dilapidated and almos wasted
3 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | WZPDCL | Yes | 70 | 150 | 300 | Not in Good Situation, Maintenance and Service is Needed. | 10 | 15 | 2 | 0 | HT Cable - 3C X 50 Sqmm, LT Cable - 4 X 25 sqmm, 25 meter(Approximate) | Concealed Wiring | Dilapidated and almost wasted
4 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | REB | Yes |  | 0 | 0 | no | 10 | 50 |  | 0 | 20rm wap ,12 meter, | Dilapidated | Dilapidated and almos wasted
5 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal | REB | Yes | 70 | 150 | 300 | Good | 5.5 | 20 | 0 | 0 | HT Cable - 3C X 50 Sqmm, LT Cable - 4 X 25 sqmm, 25 meter(Approximate) | Concealed Wiring
6 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola

## Ancillary EM Items
SL No | Office | District Name | Name of the Hospital | Upazilla | Presence of Medical Gas System | Capacity of Medical Gas Plant if any (LPM) | Number of bed having Medical Gas Facility if any (nos) | Medical Gas Related Additional Info (describe) | Presence of Compound and Security Light | Presence of Sound and PA System | Presence of computer networks | Presence of PABX System | Presence of CCTV system | Number of Neon Poly sign board | Requirement of any ancillary items (Describe in detail) | Remarks (For any Additional Information)
1 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazila Health complex | chitalmari | No |  | 16 | There is only oxygen supply for 16 beds | No | No | No | No | Yes | 1
2 | Division - Bagerhat PWD Division | Bagerhat | Kachua Upazila Health complex | kachua | No |  | 10 | There is only oxygen supply for 10 beds | No | No | No | No | Yes | 1
3 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Yes | 0 | 10 | 10 Nos Oxygen Cylinder is Available Only | Yes | Yes | Yes | No |  | 1 | Needed a Full Functional Incineration Type Medical Gas Plant, Addressable Sound System, PABX System and 3 Nos 16 Chanel CCTV System
4 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | No |  | 0 |  | No | No | No | No | Yes | 2
5 | Division - Bagerhat PWD Division | Bagerhat | Rampal Upazila Health Complex, Bagerhat. | rampal | Yes | 0 | 30 | 30 Nos Oxygen Cylinder is Available Only | Yes | Yes | Yes | No | Yes | 1 | Needed a Full Functional Incineration Type Medical Gas Plant, Addressable Sound System, PABX System and 3 Nos 16 Chanel CCTV System
6 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola

## Other Buildings
SL No | Office | District Name | Name of the Hospital | Upazilla | Building Name | Building No (if any) | Year of Construction | Number of Floors | Plinth Area (sqft) | Total Floor Area (sqft) | Current Condition (Describe) | Floor Plan (if any) | Visual Evidence (Image and Video) | Remarks (Additional Information)
1 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Fakirhat Upazila Health Complex | fakirhat | OPD Block |  | 1965 | 2 | 7012.46 | 11732.46 |  | No file | No file | Old damaged unserviceable Building
2 | Division - Bagerhat PWD Division | Bagerhat | 50 Bed Mollahat Upazila Health Complex | mollahat | OPD Block |  | 1965 | 2 | 7012.46 | 11732.46 | Old damaged unserviceable Building | 1 pdf | No file
3 | Division - Bagerhat PWD Division | Bagerhat | Chitalmari Upazilla Health Complex | chitalmari | admin building | 1 | 1998 | 2 | 11240 | 22480 | minar cracks were visible in some portions of the walls. Overall, the current condition of the building is satisfactory | No file | 1 mp4
4 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | UHFPO |  | 1985 | 1 | 1242 | 1242 |  | No file | No file
5 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | 4TH CLASS QUARTER |  | 1984 | 1 | 4312 | 4312 |  | No file | No file
6 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | 3RD CLASS QUARTER |  | 1983 | 2 | 2905 | 5810 |  | No file | No file
7 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | NURSE QUARTER |  | 1982 | 1 | 1550 | 1550 |  | No file | No file
8 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | DOCTORS QUARTER 2 |  | 1981 | 1 | 1947 | 1947 |  | No file | No file
9 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | DOCTORS QUARTER |  | 1980 | 1 | 1947 | 1947 |  | No file | No file
10 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | HALL ROOM |  | 2005 | 1 | 1104 | 1 |  | No file | No file
11 | Division - Bagerhat PWD Division | Bagerhat | kachua Upazilla Health Complex | kachua | Oxyzen Room |  | 2005 | 1 | 264 | 264 |  | No file | No file
12 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Mosque |  | 2010 | 1 | 5600 |  |  | No file | 1 jpeg
13 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Staff Quarter |  | 1998 | 1 | 2500 | 2500 | Use | No file | 1 jpeg
14 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Nurses Quarter |  | 1998 | 2 | 2700 | 5400 | Condemned | No file | 1 jpeg
15 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Dormitory |  | 2010 | 2 | 1000 | 2000 | Use | No file | 1 jpeg
16 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Nurses Quarter |  | 1998 | 2 | 1200 | 4800 | Condemned | No file | 1 jpeg | ঝুকি নিয়ে নার্সরা বসবাস করছে।
17 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Nurses Quarter |  | 1998 | 2 | 1600 | 6400 | Use | No file | 1 jpeg
18 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | mongla | Doctors Quarter |  | 1998 | 2 | 3000 | 6000 | Running | No file | 1 jpeg
19 | Division - Bagerhat PWD Division | Bagerhat | Mongla Upazila Health Complex, Bagerhat. | morrelganj | Staff Quarter |  | 1962 | 1 | 2000 | 2000 | Condemned | No file | 1 jpeg
20 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | Dormitory |  |  | 2 | 1150 | 2300 | Running/Repair (on going) | No file | 1 jpeg
21 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | Staff Quarter |  |  | 2 | 1600 | 6400 | Unuse | No file | No file
22 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | Staff Quarter |  |  | 2 | 1700 | 3400 | Unuse | No file | 1 jpeg
23 | Division - Bagerhat PWD Division | Bagerhat | Morelgonj Upazila Health Complex | morrelganj | Doctors Quarter |  | 2020 | 2 | 2200 | 4400 | Running | No file | 1 jpeg
24 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | Mosque |  |  | 1 |  |  |  | No file | 1 jpeg
25 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | Staff Quarter |  | 1976 | 1 |  |  | Condemned | No file | 1 jpeg
26 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | Staff Quarter |  | 1976 |  | 2800 | 5600 | Running | No file | 1 jpeg
27 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | Auditorium |  | 2001 | 2 | 1350 | 2700 | Running | No file | 1 jpeg
28 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | Nurses Quarter |  | 1976 | 2 | 2600 | 5200 | Running | No file | 1 jpeg
29 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | Nurses Quarter |  | 2001 | 2 | 1300 | 2600 | Running | No file | 1 jpeg
30 | Division - Bagerhat PWD Division | Bagerhat | Sharonkhola Upazila Health Complex, Bagerhat. | sarankhola | Doctors Quarter |  | 2001 | 2 | 3600 | 7200 | Running | No file | 1 jpeg